{"text_format":"1","workbook":"xlsx","n_sheets":6,"sheets":["Schakelbericht Opdracht A","Schakelbericht Opdracht B","Status&Handelingen","Componenten","Standaard taalgebruik","Blad1"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":5,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Schakelbericht Opdracht A","index":0,"n_rows":22,"n_cols":15,"rows_kept":22,"cut":false,"hidden":false,"merged":[[21,2,21,3],[13,11,13,14],[14,1,14,3],[14,4,14,5],[14,6,14,7],[14,11,16,14],[15,1,15,7],[15,8,15,10],[16,2,16,3],[16,5,16,7],[16,9,16,10],[13,1,13,5],[13,6,13,8],[13,9,13,10],[21,5,21,7],[21,9,21,10],[17,11,17,14],[18,2,18,3],[18,5,18,7],[18,9,18,10],[18,11,19,14],[19,2,19,3],[19,5,19,7],[19,9,19,10],[17,2,17,3],[17,5,17,7],[17,9,17,10],[20,2,20,3],[20,5,20,7],[20,9,20,10],[20,11,21,14],[10,14,11,14],[10,1,11,1],[10,2,11,2],[10,3,11,3],[10,4,11,4],[10,5,11,5],[10,7,11,7],[10,8,11,8],[10,9,11,9],[10,11,11,11],[10,12,11,12],[10,13,11,13],[8,14,9,14],[8,1,9,1],[8,2,9,2],[8,3,9,3],[8,4,9,4],[8,5,9,5],[8,7,9,7],[8,8,9,8],[8,9,9,9],[8,11,9,11],[8,12,9,12],[8,13,9,13],[6,14,7,14],[6,1,7,1],[6,2,7,2],[6,3,7,3],[6,4,7,4],[6,5,7,5],[6,7,7,7],[6,8,7,8],[6,9,7,9],[6,11,7,11],[6,12,7,12],[6,13,7,13],[4,14,5,14],[2,1,2,3],[2,4,2,9],[2,10,2,11],[2,12,2,14],[4,1,5,1],[4,2,5,2],[4,3,5,3],[4,4,5,4],[4,5,5,5],[4,7,5,7],[4,8,5,8],[4,9,5,9],[4,11,5,11],[4,12,5,12],[4,13,5,13],[0,1,0,3],[0,4,0,12],[0,13,0,14],[1,1,1,3],[1,4,1,9],[1,10,1,14]]}
[null,"                              ",null,null,"STIPEL Uniform schakelbericht - Model bèta",null,null,null,null,null,null,null,null,"  Versie 20260101"]
[null,"Datum:",null,null,"Aard en plaats van de werkzaamheden",null,null,null,null,null,"Aard van de schakelhandelingen:"]
[null,null,null,null,"Opdracht A: Kabel uit bedrijf nemen tussen LVK 2.1 en LVK 2.2",null,null,null,null,null,"Uit bedrijf nemen"]
[null,"Nr.","Spanning","Locatie","Veld","Richting","Test en/of meting","Borging","Schakel- en/of beveiligingscomponenten","(Schakel)handeling","Test en/of meting","Borging","Gevolg","Bijzonderheden","Gereed"]
[null,1,"LS","LVK 2.2",3,"LVK 2.1","CSWS","BA"]
[]
[null,2,"LS","LVK 2.1",6,"LVK 2.2",null,null,"Vermogensschakelaar met scheidingsfunctie","Afschakelen en scheiden","SLA","BA","Afgeschakeld en gescheiden"]
[]
[null,3,"LS","LVK 2.1",6,"LVK 2.2","SLA",null,"Aardingsgarnituur","Aarden en kortsluiten",null,null,"Aarding en kortsluiting aangebracht"]
[]
[null,4,"LS","LVK 2.2",3,"LVK 2.1","SLA",null,"Aardingsgarnituur","Aarden en kortsluiten",null,null,"Aarding en kortsluiting aangebracht"]
[]
[]
[null,"Opgesteld door (kandidaat):",null,null,null,null,"Installatieverantwoordelijke (IV)\n(hoeft niet te worden ingevuld)",null,null,"Werkverantwoordelijke (WV)\n(hoeft niet te worden ingevuld)",null,"Schakelhandelingen uitgevoerd (hoeft niet te worden ingevuld)"]
[null,"Naam: STIPEL",null,null,"Paraaf: STIPEL",null,"Naam:",null,"Paraaf:","Naam: ","Paraaf:","Naam:\nDatum:\nParaaf:"]
[null,"Afkortingen Test en/of meting",null,null,null,null,null,null,"Afkortingen Borging"]
[null,"AAB","Aantonen afwezigheid bedrijfsspaning",null,"FA","Fasegelijkheid aantonen",null,null,"BA","Beveiligen tegen opnieuw inschakelen en bord of label plaatsen"]
[null,"BPR","Beproeven",null,"IM","Isolatieweerstand meten",null,null,"BV","Beveiliging tegen opnieuw inschakelen verwijderen en bord of label verwijderen",null,"Schakelhandelingen gecontroleerd (hoeft niet te worden ingevuld)"]
[null,"CS","Controleren op spanning",null,"SM","Spanning meten",null,null,null,null,null,"Naam:\nDatum:\nParaaf: "]
[null,"CSWS","Controleren op spanning aan weerszijden van de schakelaar",null,"SLA","Spanningsloosheid aantonen"]
[null,"DR","Draairichting beoordelen",null,"SEL","Selecteren kabel",null,null,null,null,null,"Opmerkingen (hoeft niet te worden ingevuld):"]
[null,"DV","Draaiveld bepalen"]

{"sheet":"Schakelbericht Opdracht B","index":1,"n_rows":22,"n_cols":15,"rows_kept":22,"cut":false,"hidden":false,"merged":[[0,1,0,3],[0,4,0,12],[0,13,0,14],[1,1,1,3],[1,4,1,9],[1,10,1,14],[4,14,5,14],[2,1,2,3],[2,4,2,9],[2,10,2,11],[2,12,2,14],[4,1,5,1],[4,2,5,2],[4,3,5,3],[4,4,5,4],[4,5,5,5],[4,7,5,7],[4,8,5,8],[4,9,5,9],[4,11,5,11],[4,12,5,12],[4,13,5,13],[6,14,7,14],[6,1,7,1],[6,2,7,2],[6,3,7,3],[6,4,7,4],[6,5,7,5],[6,7,7,7],[6,8,7,8],[6,9,7,9],[6,11,7,11],[6,12,7,12],[6,13,7,13],[8,14,9,14],[8,1,9,1],[8,2,9,2],[8,3,9,3],[8,4,9,4],[8,5,9,5],[8,7,9,7],[8,8,9,8],[8,9,9,9],[8,11,9,11],[8,12,9,12],[8,13,9,13],[10,14,11,14],[10,1,11,1],[10,2,11,2],[10,3,11,3],[10,4,11,4],[10,5,11,5],[10,7,11,7],[10,8,11,8],[10,9,11,9],[10,11,11,11],[10,12,11,12],[10,13,11,13],[21,9,21,10],[17,11,17,14],[18,2,18,3],[18,5,18,7],[18,9,18,10],[18,11,19,14],[19,2,19,3],[19,5,19,7],[19,9,19,10],[17,2,17,3],[17,5,17,7],[17,9,17,10],[20,2,20,3],[20,5,20,7],[20,9,20,10],[20,11,21,14],[21,2,21,3],[13,11,13,14],[14,1,14,3],[14,4,14,5],[14,6,14,7],[14,11,16,14],[15,1,15,7],[15,8,15,10],[16,2,16,3],[16,5,16,7],[16,9,16,10],[13,1,13,5],[13,6,13,8],[13,9,13,10],[21,5,21,7]]}
[null,"                              ",null,null,"STIPEL Uniform schakelbericht - Model bèta",null,null,null,null,null,null,null,null,"  Versie 20260827"]
[null,"Datum:",null,null,"Aard en plaats van de werkzaamheden",null,null,null,null,null,"Aard van de schakelhandelingen:"]
[null,null,null,null,"Opdracht B: Motor M12 en kabel in bedrijf nemen",null,null,null,null,null,"In bedrijf nemen"]
[null,"Nr.","Spanning","Locatie","Veld","Richting","Test en/of meting","Borging","Schakel- en/of beveiligingscomponenten","(Schakel)handeling","Test en/of meting","Borging","Gevolg","Bijzonderheden","Gereed"]
[null,1,"LS","LVK 2.2",4,"WS","IM","BV","Vermogensschakelaar","Scheiding opheffen",null,null,"Scheiding opgeheven"]
[]
[null,2,"LS","LVK 2.2",4,"WS",null,null,"Vermogensschakelaar","Onder spanning brengen",null,null,"Onder spanning gebracht"]
[]
[null,3,"LS","WS",null,"LVK 2.2",null,"BV","Werkschakelaar","Onder spanning brengen",null,null,"Onder spanning gebracht"]
[]
[null,4,"LS","M 12",null,null,"DR"]
[]
[]
[null,"Opgesteld door (kandidaat):",null,null,null,null,"Installatieverantwoordelijke (IV)\n(hoeft niet te worden ingevuld)",null,null,"Werkverantwoordelijke (WV)\n(hoeft niet te worden ingevuld)",null,"Schakelhandelingen uitgevoerd (hoeft niet te worden ingevuld)"]
[null,"Naam: STIPEL",null,null,"Paraaf: STIPEL",null,"Naam:",null,"Paraaf:","Naam: ","Paraaf:","Naam:\nDatum:\nParaaf:"]
[null,"Afkortingen Test en/of meting",null,null,null,null,null,null,"Afkortingen Borging"]
[null,"AAB","Aantonen afwezigheid bedrijfsspaning",null,"FA","Fasegelijkheid aantonen",null,null,"BA","Beveiligen tegen opnieuw inschakelen en bord of label plaatsen"]
[null,"BPR","Beproeven",null,"IM","Isolatieweerstand meten",null,null,"BV","Beveiliging tegen opnieuw inschakelen verwijderen en bord of label verwijderen",null,"Schakelhandelingen gecontroleerd (hoeft niet te worden ingevuld)"]
[null,"CS","Controleren op spanning",null,"SM","Spanning meten",null,null,null,null,null,"Naam:\nDatum:\nParaaf: "]
[null,"CSWS","Controleren op spanning aan weerszijden van de schakelaar",null,"SLA","Spanningsloosheid aantonen"]
[null,"DR","Draairichting beoordelen",null,"SEL","Selecteren kabel",null,null,null,null,null,"Opmerkingen (hoeft niet te worden ingevuld):"]
[null,"DV","Draaiveld bepalen"]

{"sheet":"Status&Handelingen","index":2,"n_rows":44,"n_cols":10,"rows_kept":44,"cut":false,"hidden":true,"merged":[[0,3,0,4],[0,5,0,6]]}
["Locatie","Spanning","Veld","Test en/of meting",null,"Borging",null,"Wat is de schakelhandeling","Wat is het gevolg","Aard van de schakelhandelingen"]
[]
["G 1","LS",1,"AAB","AAB - Aantonen afwezigheid bedrijfsspanning","BA","BA - Beveiligen tegen opnieuw inschakelen en bord of label plaatsen","Aarden en kortsluiten","Aarding en kortsluiting aangebracht","In bedrijf nemen"]
["G 10","HS",2,"BPR","BPR - Beproeven","BV","BV - Beveiliging tegen opnieuw inschakelen verwijderen en bord of label verwijderen","Afschakelen","Afgeschakeld","Uit bedrijf nemen"]
["G 2",null,3,"CS","CS - Controleren op spanning","BIAA","BIAA - Bord \"Let op installatie is geaard\" aanbrengen","Afschakelen en scheiden","Afgeschakeld en gescheiden"]
["HS 1",null,4,"CSWS","CSWS - Controleren op spanning aan weerszijden \nvan de schakelaar","BIAV","BIAV - Bord \"Let op installatie is geaard\"\nverwijderen","Afschermen","Afgeschermd"]
["HS 1.1",null,5,"DR","DR - Draairichting beoordelen",null,null,"Afschermingen wegnemen","Afschermingen weggenomen"]
["HS 1.1.2",null,6,"DV","DV - Draaiveld bepalen",null,null,"Inschakelen","Gekoppeld"]
["HS 1.1.3",null,7,"FA","FA - Fasegelijkheid aantonen",null,null,"Koppelen","Gekoppeld met scheidingsfunctie"]
["HS 2",null,null,"IM","IM - Isolatieweerstand meten",null,null,"Koppelen met scheidingsfunctie","Gescheiden"]
["HS 2.1",null,null,"SM","SM - Spanning meten",null,null,"Kortsluiting en aarding verwijderen","Ingeschakeld"]
["HS 2.1.3",null,null,"SLA","SLA - Spanningsloosheid aantonen",null,null,"Onder spanning brengen","Kortsluiting en aarding verwijderd"]
["LS 1",null,null,"SEL","SEL - Selecteren kabel",null,null,"Ontkoppelen","Onder spanning gebracht"]
["LS 2",null,null,null,null,null,null,"Ontkoppelen met scheidingsfunctie","Ontkoppeld"]
["LS 3",null,null,null,null,null,null,"Ring openen","Ontkoppeld met scheidingsfunctie"]
["LVK 1",null,null,null,null,null,null,"Ring openen en scheiden","Ring geopend"]
["LVK 2",null,null,null,null,null,null,"Ring sluiten","Ring geopend en gescheiden"]
["LVK 2.1",null,null,null,null,null,null,"Ring sluiten en scheiding opheffen","Ring gesloten"]
["LVK 2.1.2",null,null,null,null,null,null,"Scheiden","Ring gesloten en scheiding opgeheven"]
["LVK 2.2",null,null,null,null,null,null,"Scheiding opheffen","Scheiding opgeheven"]
["LVK 3",null,null,null,null,null,null,"Scheiding opheffen en onder spanning brengen","Scheiding opgeheven en onder spanning gebracht"]
["LVK 3.1",null,null,null,null,null,null,"Uitschakelen","Uitgeschakeld"]
["M 1"]
["M 10"]
["M 11"]
["M 12"]
["M 13"]
["M 14"]
["M 15"]
["M 2"]
["M 3"]
["M 4"]
["M 5"]
["M 6"]
["T 1"]
["T 2"]
["T 3"]
["T 4"]
["T 5"]
["T10"]
["UPS"]
["WCD 10"]
["Zonnepaneel G"]
["WS"]

{"sheet":"Componenten","index":3,"n_rows":12,"n_cols":1,"rows_kept":12,"cut":false,"hidden":true,"merged":[]}
["Welke schakel- en/of beveilingscomponenten "]
["Aardingsgarnituur"]
["Lastschakelaar"]
["Lastscheider"]
["Scheider"]
["Smeltpatroonlastschakelaar"]
["Smeltpatroonlastscheider"]
["Smeltpatroonscheider"]
["Smeltveiligheid"]
["Vermogensschakelaar"]
["Vermogensschakelaar met scheidingsfunctie"]
["Werkschakelaar"]

{"sheet":"Standaard taalgebruik","index":4,"n_rows":23,"n_cols":2,"rows_kept":23,"cut":false,"hidden":true,"merged":[]}
["NEN 3140","NEN 3840"]
["  aarden en kortsluiten","  aantonen afwezigheid bedrijfsspanning"]
["  afschakelen","  aarden en kortsluiten"]
["  afschermen","  afschakelen"]
["  afschermingen wegnemen","  afschermen"]
["  beveiligen tegen opnieuw inschakelen en bord of label plaatsen","  afschermingen wegnemen"]
["  beveiliging tegen opnieuw inschakelen verwijderen en bord of label verwijderen","  beveiligen tegen opnieuw inschakelen en bord of label plaatsen"]
["  controleren op spanning","  beveiliging tegen opnieuw inschakelen verwijderen en bord of label verwijderen"]
["  fasegelijkheid aantonen","  controleren op spanning"]
["  inschakelen","  fasegelijkheid aantonen"]
["  isolatieweerstand meten","  inschakelen"]
["  koppelen","  isolatieweerstand meten"]
["  kortsluiting en aarding verwijderen","  koppelen"]
["  onder spanning brengen","  kortsluiting en aarding verwijderen"]
["  ontkoppelen","  onder spanning brengen"]
["  ring openen","  ontkoppelen"]
["  ring sluiten","  ring openen"]
["  scheiden","  ring sluiten"]
["  scheiding opheffen","  scheiden"]
["  spanning meten","  scheiding opheffen"]
["  spanningsloosheid aantonen","  spanning meten"]
["  uitschakelen","  uitschakelen"]
[null,"  werkaarding"]

{"sheet":"Blad1","index":5,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":true,"merged":[]}